Type: DVN 225 D2 30

Item number: 144875

Description:

Centrifugal roof fan with backward curved impeller and vertical discharge. Housing made of weather-resistant aluminium AlMg3. The air outlet is protected by a protection grille against intrusion, birds, dirt and other foreign objects. Baseplate of galvanized steel sheet with deep drawn air inlet and preassembled screws for the possibility of connecting pipe flanges and accessories according to DIN 24154 / EN 12 220. The fan has been conceived for easy mounting on roof socket (optional accessory) without the necessity of removing the housing. Swing-out fan unit for cleaning and maintenance purposes. Suited for use according to VDI 2052. The incorporated grease pan and drain avoid roof soiling and ensure a controlled drainage of fat impregnated impurities.

The efficiency-optimized radial impeller with backward curved blades is fitted on the shaft of an IEC three phase motor with a special shaft seal that prevents the ingress of oil and water. The impeller is provided with a Taperlock clamping bush which ensures improved balancing quality and higher operational stability. The impeller is balanced together with the motor according to the quality class G 6.3 of DIN / ISO 1940, on 2 planes. Speed control possible only via frequency converter. The drive motor is placed outside of the airstream. For maintenance-free use, there are ball bearings with lifetime lubrication, sealed on both sides. The motor thermal protection must be installed on site (monitoring of the thermal motor current via a FU or motor protection switch). The electrical connection is to be done via the integrated isolator switch.

CE marking according to EC Declaration of Conformity for Electromagnetic Compatibility EMC - Directive 2004/108/EC. EC - Declaration of Incorporation according to the Machinery Directive 2006/42/EC - Directive 2009/125/EC (Reg.

1253/2014/EU).

Technical data:

Volumetric flow (V): m³/h Pressure increase (Δp fa): Pa Efficiency static max. (η fa): 43,6 % Efficiency total max. (ηt): 44,6 %

Rated voltage (U): 400, 3~ V Rated frequency (f): 50 Hz Rated power consumption (P N): 284 W Current consumption max. (I max.): 0,8 A Rated speed (n): 2930 min-1

Protection class motor: IP 55

Protection class terminal box: IP - Ambient temperature max. (t A): 50 °C Medium temperature max. (tM): 120 °C

Inlet sound power level (L WA5): 77 dB(A) Outlet sound power level (LWA6): 80 dB(A)

Dimensions housing (L x W x H): 514x514x482 mm

Weight: 28,5 kg

Wiring diagram: 143654

Manufacturer:

ruck Ventilatoren GmbH Max-Planck-Str. 5

97944 Boxberg

Tel. 07930-9211300 [www.ruck.eu](http://www.ruck.eu/)

Type: DVN 225 D2 30

Item number: 144875

|  |  |  |
| --- | --- | --- |
| Available accessories:DSF 220-10 | 126170 | Roof socket, flat roof, size 220 |
| DSF 220-12 up to 19 |  | Sloped roof socket, size 220, slope optional in 3° increments (3-24°) |
| DSS 220-10 | 126356 | Roof socket, flat roof sound insulated, size 220 |
| DSS 220-12 up to 19 |  | Sloped roof sound insulated socket, size 220, |
|  |  | slope optional in 3° increments (3-24°) |
| DAP 220 | 133946 | Roof adapter plate size 220 |
| DVK 180 10 | 153000 | Roof - Gravity shutter size 180 |
| DAS 180 F4 | 145422 | Roof - Inlet spigot size 180 |
| DAF 150 | 110735 | Roof - Inlet flange size 150 |
| DAF 160 | 137396 | Roof - Inlet flange size 160 |
| DAF 180 | 110744 | Roof - Inlet flange size 180 |
| MS 01 | 140407 | Motor protection switch with device switch function |
| FU 075 08 | 141836 | Frequency controller, output voltage 0-230V, 3~, 750W, IP20 |
| FU 075 14 | 141847 | Frequency controller, output voltage 0-230V, 3~, 750W, IP66 |
| FU 075 20 | 141858 | Frequency controller, output voltage 0-400V, 3~, 750W, IP20 |
| FU 075 26 | 141869 | Frequency controller, output voltage 0-400V, 3~, 750W, IP66 |
| MTP 20 | 128146 | Potentiometer 0-10V, stepless |
| MTP 30 | 143289 | Stepped potentiometer, +10Vdc, step 1+2 adjustable, step 3 100% Vdc |
| MTP 40 | 147359 | Potentiometer for connection in terminal box, sales unit 20 pcs. |
| CON P1000 | 115259 | Constant pressure control with day-night switch function |
| CLIMASET01 | 111314 | Accessories set for CON P1000, pressure hose, nipples and screws |
| SEN AIR | 148641 | Airflow and temperature transducer |